## Slide 1: RDS Webinar RDS+61850
Erik Wiborg, 2024

## Slide 2
1. RDS implementation at Statkraft

## Slide 3
Purchasing
Maintenance
Risk management
Process Control
Asset management
Asset condition monitoring
Documentation
Information availability
System information management
…

## Slide 4
- Product
= Function
+ Location
%Type
Notes: Så tett opp til logo som standarden har å by på
Tenk prosessdiagram, enlinjeskjema
Tenk Kart, planoversikt
Tenk sammenstillingstegning, IKEA

## Slide 5
RDS + 61850
Process
Local Control
Remote Control
Network Mngr
(End user)
Dispatch
Operation path
Production
Local data collection
Analysis path
Data Acquisition
CDP
Data analysis
(End user)
OneView
Maintenance

## Slide 6: Implementation principles:
Step-by-step
Only what is relevant
(signals)

## Slide 8
TRANSLATION
NAMED SIGNALS
JOST.AGG1.TURB1.TRBLAG.F_OLNIVHOY
<JOST.PS1>=A1.JF1.KJ3.FRA1.BLA1/SLVL1.Hi1.stVal
Turbine bearing oil level high alarm
Notes: Deep learning
Generative AI

## Slide 9
Interesting for maintenance
Notes: Deep learning
Generative AI

## Slide 11
Named signal list
Example Powerplant
Guidelines
>
>
https://github.com/ErikJacquesWiborg/RDS-PS

## Slide 12
2. RDS implementation principles for Signal modelling

## Slide 13
AA - “Support frame system”

## Slide 14
=A1.KA1
=A1.RB1
=A1 Unit 1
=H3 Unit bypass
KA1

## Slide 15
=A1.KA1
=A1.RB1
P
=A1.KA1.BPA2 Main Valve outlet pressure
=A1.RB1.BPA1 Turbine Inlet pressure

## Slide 16
Instantiation (numbering) shall not hold any meaning
mostly

## Slide 17
FILTER
P
BPA1
Pressure measurement upstream
BPA2
Pressure measurement downstream
P

## Slide 20
1
2

## Slide 21
RDS and signals

## Slide 22
Functional aspect: Leaves are signals/data streams

## Slide 23
Upper Guide Bearing
Signal description
Signals attach to the source
A1.JF1.KJ1.BSG1/SVBR1.Vbr.mag
Accelerometer
A1.JF1.KJ1 /SVBR1.Vbr.mag
Notes: 61850 - Layered approach

## Slide 24
=D1.CMA1 (Tank)
=D1.CMA1.BLA1 (Smart level measurement)
=D1.CMA1.BLA1.BPA1 (Pressure)
=D1.CMA1.BLA1.BPA2 (Pressure)
=D1.CMA1.BLA1.BPA2 /TPRS1.Prs.mag
=D1.CMA1.BLA1/SLVL1.Lo2.stVal (low level alarm)
Functional Hierarchy for smart measurement systems

## Slide 25
3. Introduction to IEC 61850-7

## Slide 26
What?
Where?
42
Object reference
Signal Description
IEC/ISO 81346
IEC 61850

## Slide 27
=A1.KA1.KA / KVLV1 . OpnPos . stVal & [ST]
Logical Node
Data Object
Data attributes
Functional Constraint
RDS
Notes: K: Code for Mechanical equipement
StVal : Status Value

## Slide 28: Logical Node
IEC 61850-7-4
IEC 61850-7-410
?
Signal Main Function Group
=A1.KA1.KA/KVLV1.OpnPos.stVal[ST]

## Slide 29
Equipment control
Temperature monitoring
Alarm handling
HMI

## Slide 30: ABCD1
Class
Name abbreviation
Instantiation
VLV: Valve
BRC: Breaker
TMP: Temperature

## Slide 31: Logical Node – 61850-7-4

## Slide 32: Logical Node

## Slide 33: Data objects
IEC 61850-7-4 (Nodes)
IEC 61850-7-4 (ch.6, Table 10)
?
Nature of the signal
=A1.KA1.KA/KVLV1.OpnPos.stVal[ST]

## Slide 34: Data Objects

## Slide 35: Data Objects
=A1.KA1
Logical Device
/KVLV1
Logical Node
.OpenPos
Data Object
Information – NOT PART OF TAG

## Slide 36: Common data class
IEC 61850-7-3
?
Data Object Category
=A1.KA1.KA/KVLV1.OpnPos.stVal[ST]
SPS

## Slide 37: Common data class (61850-7-3)

## Slide 38: Common data class
=A1.KA1.KA/KVLV1.OpnPos.stVal[ST]

## Slide 39: Data Attribute
IEC 61850-7-3 (CDC)
IEC 61850-7-3 (ch.8 - table 64)
?
Signal description

## Slide 42: Functional contraint
IEC 61850-7-3 , Annex B
?
General information type
=A1.KA1.KA/KVLV1.OpnPos.stVal[ST]

## Slide 43: Functional Constraints
see 61850-7-3 , Annex B

## Slide 44
…/STMP1.Tmp.mag Temperature Magnitude
…/STMP1.Hi1.stVal Temperature high, alarm
…/STMP1.Hi2.stVal Temperature high, trip

## Slide 45
A1.JE1.KF1/SIML1.CmbuGas.mag
Unit transformer measurement of total dissolved combustible gases (TDCG)
A1.JF1.KJ1.EGC1.BTA1/STMP1.Hi1.stVal Upper guide bearing, cooler 1, cooling water temperature, alarm

## Slide 46
Layered hierarchy

## Slide 47: Flexible Precise Unambiguous Generic
https://github.com/ErikJacquesWiborg/RDS-PS