## Sheet1
Statkraft
Version 04.06.2024
RDS | [6 empty] | 61850 |  |  |  | Description | Keywords
P1 | T1 | T2 | T3 | C1 | C2 | C3 | LN |  | DO | DA
A@ | RA1 | LD1 |  |  |  |  | AFVC | 1 | ReqVol | mxVal.f | Excitation system field voltage set-point | Feltspenning setpunkt, mtrafo
A@ | RA1 | LD1 |  |  |  |  | AFVV | 1 | VolSpt | mxVal.f | Excitation system field voltage set-point by operator | Feltspenning setpunkt operatør, mtrafo
A@ | RB1 | LD1 |  |  |  |  | HWMX | 1 | ReqWMax | mag.f | Turbine YMax set-point | Ymaks setpunkt
A@ | RB1 | PF1 |  |  |  |  | HDFL | 1 | PosPct | mag.f | Turbine deflector position | Deflektor
A@ | RB1 | LD1 |  |  |  |  | HWMX | 1 | ReqWMax | mag.f | Turbine power limiter set-point | Effektbegrenser, maksbegrenser
A@ | RB1 | LD1 |  |  |  |  | HSPC | 1 | SpdEsp | mag.f | Turbine frequency set-point
A@ | RB1 | LD1 |  |  |  |  | HSPC | 1 | DrpEsp | mag.f | Turbine droop set-point | Statikk setpunkt
A@ | RB1 | LD1 |  |  |  |  | HSPC | 1 | SpdSpt | mxVal.f | Turbine frequency set-point by operator
A@ | RB1 | LD1 |  |  |  |  | HSPC | 1 | DrpSpt | mxVal.f | Turbine droop set-point by operator | Statikk setpunkt operatør
A@ | RB1 | LD1 |  |  |  |  | HFLC | 1 | ReqFlw | mag.f | Turbine load set-point | Last innstilling, last settpunkt
A@ | JF1 | KA1 |  |  |  |  | HMBR | 1 | ProtBrkOn | stVal | Mechanical brake on due to protection event | Brems på under drift, unormal
A@ | JF1 | KA1 |  |  |  |  | HMBR | 1 | BrkOff | stVal | Mechanical brake off | Brems
A@ | JF1 |  |  | RLC1 |  |  | AAVR | 1 | ElBrk | stVal | Electrical brake on
A@ | JF1 |  |  | RLC1 |  |  | AAVR | 1 | ElBrkBlk | stVal | Electrical brake function blocked | Elekstrisk brems blokkert
A@ | RB1 | [5 empty] | HNHD | 1 | Nhd | mag.f | Water net head | Fallhøyde
A@ | JF1 | KA1 |  |  |  |  | HSPD | 1 | SpdBrk2 | stVal | Emergency brake speed
A@ | JF1 | LE1 |  |  |  | BSE@ | SSPD | 1 | SpdPct | mag.f | Rotational speed (%) measurement
A@ | JF1 | LE1 |  |  |  | BSE@ | SSPD | 1 | Spd | mag.f | Rotational speed measurement
A@ | JF1 | LE1 |  |  |  |  | HSPD | 1 | SpdCrp | stVal | Creep detection alarm | Kryp
A@ | JF1 | LE1 |  |  |  |  | HSPD | 1 | SpdMechOv | stVal | Mechanical over-speed detection | Rusing, rusevern
A@ | RB1 | KA1 |  |  |  |  | HNDL | 1 | PosPct | mag.f | Needle position in percent | Nål, dyse, jet
A@ | RB1 | KA1 |  |  |  |  | HTGV | 1 | PosCls | stVal | Guide vanes closed | Ledeapperat, ledeskovl
A@ | RB1 | KA1 |  |  |  |  | HTGV | 1 | PosOpn | stVal | Guide vanes open | Ledeapperat, ledeskovl
A@ | KA1 | [5 empty] | HVLV | 1 | Pos | stVal | Main valve position | Hovedventil, MIV, kuleventil
A@ | KA1 | [5 empty] | HVLV | 1 | PosCls | stVal | Main valve closed | Hovedventil, MIV, kuleventil
A@ | KA1 | [5 empty] | HVLV | 1 | DvAlm | stVal | Main valve stuck | Hovedventil, MIV, kuleventil
A@ | RA1 | LD1 |  |  |  |  | MMDC | 1 | Amp | mag.f | Excitation system current | Magnetiseringsstrøm, feltstrøm
A@ | RA1 | LD1 |  |  |  |  | AFCG | 1 | ReqAmp | mag.f | Excitation system current set-point
A@ | RA1 | LD1 |  |  |  |  | MMDC | 1 | Vol | mag.f | Excitation system voltage
A@ | RA1 | LD1 |  |  |  |  | AFCG | 1 | AmpStp | mag.f | Excitation system current set-point by operator
A@ | RA1 | [5 empty] | MMXU | 1 | TotPF | mag.f | Generator power factor (Cos phi) | Cos phi
A@ | RA1 | [5 empty] | MMXU | 1 | Hz | mag.f | Generator frequency
A@ | RA1 | [5 empty] | MMXU | 1 | AvPPVPhs | mag.f | Generator voltage
A@ | RA1 | LD1 |  |  |  |  | AUCG | 1 | VolSpt | mxVal.f | Generator voltage set-point by operator
A@ | RA1 | [5 empty] | MMXU | 1 | PPV.phsAB | cVal.mag.f | Generator voltage L1-L2
A@ | RA1 | [5 empty] | MMXU | 1 | PPV.phsBC | cVal.mag.f | Generator voltage L2-L3
A@ | RA1 | [5 empty] | MMXU | 1 | PPV.phsCA | cVal.mag.f | Generator voltage L3-L1
A@ | RA1 | [5 empty] | MMXU | 1 | PNV.phsA | cVal.mag.f | Generator voltage L1-N
A@ | RA1 | [5 empty] | MMXU | 1 | PNV.phsB | cVal.mag.f | Generator voltage L2-N
A@ | RA1 | [5 empty] | MMXU | 1 | PNV.phsC | cVal.mag.f | Generator voltage L3-N
A@ | RA1 | LD1 |  |  |  |  | HWGC | 1 | ReqW | mag.f | Generator active power set-point
A@ | RA1 | LD1 |  |  |  |  | AVRG | 1 | VArSpt | mxVal.f | Generator reactive power set-point by operator | Operatør, Settpunkt, innstilling, reference
A@ | RA1 | [5 empty] | MMXU | 1 | A.phsA | cVal.mag.f | Generator current L1
A@ | RA1 | [5 empty] | MMXU | 1 | A.phsB | cVal.mag.f | Generator current L2
A@ | RA1 | [5 empty] | MMXU | 1 | A.phsC | cVal.mag.f | Generator current L3
A@ | RA1 | [5 empty] | MMXU | 1 | AvAPhs | mag.f | Generator avg current of the 3 phases
A@ | RA2 | [5 empty] | MMXU | 1 | AvAPhs | mag.f | Start motor avg current of the 3 phases
A@ | RA2 | [5 empty] | MMXU | 1 | AvPPVPhs | mag.f | Start motor average voltage
A@ | JF1 | KJ4 | HB1 | EGC1 |  | BFA@ | SFLW | 1 | Lo1 | stVal | Thrust bearing cooling water circulation low alarm | Bærelager
A@ | JF1 | KJ4 | HB1 | EGC1 |  | BFA@ | SFLW | 1 | Lo2 | stVal | Thrust bearing cooling water circulation low trip | Bærelager
A@ | JF1 | KJ1 |  | FRA1 |  | BFA@ | SFLW | 1 | Lo2 | stVal | Upper guide bearing oil circulation low trip | Øvre styrelager
A@ | JF1 | KJ1 |  | FRA1 |  | BFA@ | SFLW | 1 | Lo1 | stVal | Upper guide bearing oil circulation low alarm | Øvre styrelager
A@ | JF1 | KJ4 | HB1 | EGC1 |  | BFA@ | SFLW | 1 | Lo1 | stVal | Thrust bearing water circulation alarm | Bærelager
A@ | JF1 | KJ4 |  | FRA1 |  | BFA@ | SFLW | 1 | Lo2 | stVal | Thrust bearing oil circulation trip | Bærelager
A@ | JF1 | KJ2 |  | EGC1 |  | BFA@ | SFLW | 1 | Lo1 | stVal | Lower guide bearing cooling water circulation alarm | Nedre styrelager
A@ | JF1 | KJ2 |  | EGC1 |  | BFA@ | SFLW | 1 | Flw | mag.f | Lower guide bearing cooling water flow | Nedre styrelager
A@ | JF1 | KJ1 |  | FRA1 |  | BLA@ | SLVL | 1 | Hi2 | stVal | Upper guide bearing oil level high trip
A@ | JF1 | KJ1 |  | FRA1 |  | BLA@ | SLVL | 1 | Lo1 | stVal | Upper guide bearing oil level low alarm
A@ | JF1 | KJ1 |  | FRA1 |  | BLA@ | SLVL | 1 | Trip | stVal | Upper guide bearing oil level trip
A@ | JF1 | KJ1 |  | FRA1 |  | BLA@ | SLVL | 1 | Lo2 | stVal | Upper guide bearing oil level low trip
A@ | JF1 | KJ2 |  | FRA1 |  | BLA@ | SLVL | 1 | Hi2 | stVal | Lower guide bearing oil level high trip
A@ | JF1 | KJ2 |  | FRA1 |  | BLA@ | SLVL | 1 | Lo1 | stVal | Lower guide bearing oil level low alarm
A@ | JF1 | KJ2 |  | FRA1 |  | BLA@ | SLVL | 1 | Trip | stVal | Lower guide bearing oil level trip
A@ | JF1 | KJ2 |  | FRA1 |  | BLA@ | SLVL | 1 | Lo2 | stVal | Lower guide bearing oil level low trip
A@ | JF1 | KJ3 |  | FRA1 |  | BLA@ | SLVL | 1 | Lev | mag.f | Turbine bearing oil level
A@ | JF1 | KJ3 |  | FRA1 |  | BLA@ | SLVL | 1 | Hi1 | stVal | Turbine bearing oil level high alarm
A@ | JF1 | KJ3 |  | FRA1 |  | BLA@ | SLVL | 1 | Lo1 | stVal | Turbine bearing oil level low alarm
A@ | JF1 | KJ3 |  | FRA1 |  | BLA@ | SLVL | 1 | Hi2 | stVal | Turbine bearing oil level high trip
A@ | JF1 | KJ3 |  | FRA1 |  | BLA@ | SLVL | 1 | Lo2 | stVal | Turbine bearing oil level low trip
A@ | JF1 | KJ4 |  | FRA1 |  | BLA@ | SLVL | 1 | Lev | mag.f | Thrust bearing oil level
A@ | JF1 | KJ4 |  | FRA1 |  | BLA@ | SLVL | 1 | Hi1 | stVal | Thrust bearing oil level high alarm
A@ | JF1 | KJ4 |  | FRA1 |  | BLA@ | SLVL | 1 | Lo1 | stVal | Thrust bearing oil level low alarm
A@ | JF1 | KJ4 |  | FRA1 |  | BLA@ | SLVL | 1 | Alm | stVal | Thrust bearing oil level alarm
A@ | JF1 | KJ4 |  | FRA1 |  | BLA@ | SLVL | 1 | Hi2 | stVal | Thrust bearing oil level high trip
A@ | JF1 | KJ4 |  | FRA1 |  | BLA@ | SLVL | 1 | Lo2 | stVal | Thrust bearing oil level low trip
A@ | JF1 | KJ4 |  | FRA1 |  | BLA@ | SLVL | 1 | Trip | stVal | Thrust bearing oil level trip
A@ | JF1 | KJ4 |  | FRA1 |  | BPC@ | SPRS | 1 | Lo2 | stVal | Thrust bearing segment @CS3 oil pressure low trip
A@ | KA1 |  |  |  |  | BPA2 | SPRS | 1 | Lo1 | stVal | Main valve outlet low pressure alarm | Turbine inlet/trommetrykk
A@ | KA1 |  |  |  |  | BPA2 | SPRS | 1 | Pres | mag.f | Main valve outlet pressure | Turbine inlet/trommetrykk
A@ | KA1 |  |  |  |  | BPA2 | SPRS | 1 | Lo2 | stVal | Main valve outlet low pressure trip | Turbine inlet/trommetrykk
A@ | RA1 | LD1 |  | XBD1 |  | BTA@ | STMP | 1 | Tmp | mag.f | Excitation system slip ring temperature | Slepering
A@ | RA1 | LD1 |  | XBD1 |  | BTA@ | STMP | 1 | Hi1 | stVal | Excitation system slip ring temperature alarm | Slepering
A@ | RA1 | LD1 |  | XBD1 |  | BTA@ | STMP | 1 | Hi2 | stVal | Excitation system slip ring temperature trip | Slepering
A@ | RA1 | HE1 |  |  |  | BTA1@ | STMP | 1 | Hi1 | stVal | Generator air cooler @CS3 cold air temperature high alarm
A@ | RA1 | HE1 |  |  |  | BTA2@ | STMP | 1 | Hi1 | stVal | Generator air cooler @CS3 warm air temperature high alarm
A@ | RA1 | HE1 |  |  |  | BTA1@ | STMP | 1 | Hi2 | stVal | Generator air cooler @CS3 cold air temperature high trip
A@ | RA1 | HE1 |  |  |  | BTA2@ | STMP | 1 | Hi2 | stVal | Generator air cooler @CS3 warm air temperature high trip
A@ | RA1 | HE1 | HB1 |  |  | BTA1 | STMP | 1 | Tmp | mag.f | Generator air coolers cold water temperature
A@ | RA1 | HE1 | HB1 |  |  | BTA2 | STMP | 1 | Tmp | mag.f | Generator air coolers warm water temperature
A@ | RA1 | LD1 |  | TAA1 |  | BTA@ | STMP | 1 | Tmp | mag.f | Excitation system core temperature | Magnetiseringstrafo, kjerne, MT
A@ | RA1 | LD1 |  | TAA1 |  | BTA@ | STMP | 1 | Hi1 | stVal | Excitation system core temperature alarm | Magnetiseringstrafo, kjerne, MT
A@ | RA1 | LD1 |  | TAA1 |  | BTA@ | STMP | 1 | Hi2 | stVal | Excitation system core temperature trip | Magnetiseringstrafo, kjerne, MT
A@ | RA1 | LD1 |  | TAA1 | TAA1 | BTA1 | STMP | 1 | Tmp | mag.f | Excitation system winding L1 temperature | Winding, vikling, fase
A@ | RA1 | RK1 | RK3 | TDA@ |  | BTA1 | STMP | 1 | Tmp | mag.f | Stator core winding @CS1 phase L3 temperature | Spor, slot, winding, vikling, statorblikk spor, fase
A@ | RA1 | RK1 | RK3 | TDA@ |  | BTA1 | STMP | 1 | Hi2 | stVal | Stator core winding @CS1 phase L3 temperature trip | Spor, slot, winding, vikling, statorblikk spor, fase
A@ | RA1 | RK1 | RK3 | TDA@ |  | BTA1 | STMP | 1 | Hi1 | stVal | Stator core winding @CS1 phase L3 temperature alarm | Spor, slot, winding, vikling, statorblikk spor, fase
A@ | JE1 | KF1 |  |  |  |  | MMXU | 1 | TotVAr | mag.f | Unit transformer reactive power | Aggregattrafo, trafo
A@ | JE1 | KF1 | KF@ | TDA1 |  | BTA1 | STMP | 1 | Hi1 | stVal | Unit transformer winding L@TS3 temperature high alarm | Winding, vikling, fase
A@ | JE1 | KF1 | KF@ | TDA1 |  | BTA1 | STMP | 1 | Hi2 | stVal | Unit transformer winding L@TS3 temperature trip | Winding, vikling, fase
A@ | JE1 | KF1 | KF@ | TDA@ |  | BTA1 | STMP | 1 | Tmp | mag.f | Unit @MS1 transformer winding L@TS3 temperature @CS1 | Winding, vikling, fase
A@ | JE1 | KF1 | HB1 |  |  | BTA1 | STMP | 1 | Hi1 | stVal | Unit transformer oil supply, oil temperature alarm
A@ | JE1 | KF1 | HB1 |  |  | BTA1 | STMP | 1 | Hi2 | stVal | Unit transformer oil supply, oil temperature trip
A@ | JE1 | KF1 | HB1 |  |  | BTA1 | STMP | 1 | Tmp | mag.f | Unit transformer oil supply, oil temperature
A@ | JE1 | KF1 | HB1 |  |  | BTA1 | STMP | 1 | Tmp | mag.f | Unit transformer oil coolers cold water temperature
A@ | JE1 | KF1 | HB1 |  |  | BTA2 | STMP | 1 | Tmp | mag.f | Unit transformer oil coolers warm water temperature
A@ | JF1 | KJ1 |  | FRA1 |  | BTA@ | STMP | 1 | Hi1 | stVal | Upper guide bearing oil temperature high alarm | Varm olje, olje temp
A@ | JF1 | KJ1 |  | FRA1 |  | BTA@ | STMP | 1 | Hi2 | stVal | Upper guide bearing oil temperature high trip | Varm olje, olje temp
A@ | JF1 | KJ2 |  | FRA1 |  | BTA@ | STMP | 1 | Tmp | mag.f | Lower guide bearing oil temperature
A@ | JF1 | KJ2 |  | FRA1 |  | BTA@ | STMP | 1 | Hi1 | stVal | Lower guide bearing oil temperature high alarm
A@ | JF1 | KJ2 |  | FRA1 |  | BTA@ | STMP | 1 | Hi2 | stVal | Lower guide bearing oil temperature high trip
A@ | JF1 | KJ2 |  | EGC@ |  | BTA1 | STMP | 1 | Tmp | mag.f | Lower guide bearing cooler @CS1 cooling water temperature
A@ | JF1 | KJ2 |  | EGC@ |  | BTA1 | STMP | 1 | Hi1 | stVal | Lower guide bearing cooler @CS1 cooling water temperature alarm
A@ | JF1 | KJ2 |  | EGC@ |  | BTA1 | STMP | 1 | Hi2 | stVal | Lower guide bearing cooler @CS1 cooling water temperature trip
A@ | JF1 | KJ3 |  | FRA1 |  | BTA@ | STMP | 1 | Tmp | mag.f | Turbine bearing oil temperature
A@ | JF1 | KJ3 |  | FRA1 |  | BTA@ | STMP | 1 | Hi1 | stVal | Turbine bearing oil temperature alarm
A@ | JF1 | KJ3 |  | FRA1 |  | BTA@ | STMP | 1 | Hi2 | stVal | Turbine bearing oil temperature trip
A@ | JF1 | KJ4 |  | FRA1 |  | BTA@ | STMP | 1 | Tmp | mag.f | Thrust bearing oil temperature
A@ | JF1 | KJ4 |  | FRA1 |  | BTA@ | STMP | 1 | Hi1 | stVal | Thrust bearing oil temperature alarm
A@ | JF1 | KJ4 |  | FRA1 |  | BTA@ | STMP | 1 | Hi2 | stVal | Thrust bearing oil temperature trip
A@ | JF1 | KJ4 |  |  |  | BTA@ | STMP | 1 | Tmp | mag.f | Thrust bearing temperature
A@ | JF1 | KJ4 |  |  |  | BTA@ | STMP | 1 | Hi1 | stVal | Thrust bearing temperature alarm
A@ | JF1 | KJ4 |  |  |  | BTA@ | STMP | 1 | Hi2 | stVal | Thrust bearing temperature trip
A@ | JF1 | KJ2 |  |  |  | BTA@ | STMP | 1 | Tmp | mag.f | Lower guide bearing temperature
A@ | JF1 | KJ2 |  |  |  | BTA@ | STMP | 1 | Hi1 | stVal | Lower guide bearing temperature alarm
A@ | JF1 | KJ2 |  |  |  | BTA@ | STMP | 1 | Hi2 | stVal | Lower guide bearing temperature trip
A@ | JF1 | KJ1 |  |  |  | BTA@ | STMP | 1 | Tmp | mag.f | Upper guide bearing temperature
A@ | JF1 | KJ1 |  |  |  | BTA@ | STMP | 1 | Hi1 | stVal | Upper guide bearing temperature alarm
A@ | JF1 | KJ1 |  |  |  | BTA@ | STMP | 1 | Hi2 | stVal | Upper guide bearing temperature trip
A@ | JF1 | KJ1 |  | FRA1 |  | BTA@ | STMP | 1 | Tmp | mag.f | Upper guide bearing oil temperature | Varm olje, olje temp
A@ | JF1 | KJ3 |  |  |  | BTA@ | STMP | 1 | Tmp | mag.f | Turbine bearing temperature
A@ | JF1 | KJ3 |  |  |  | BTA@ | STMP | 1 | Hi1 | stVal | Turbine bearing temperature alarm
A@ | JF1 | KJ3 |  |  |  | BTA@ | STMP | 1 | Hi2 | stVal | Turbine bearing temperature trip
A@ | RA2 | RK1 | RK@ | TDA1 |  | BTA@ | STMP | 1 | Tmp | mag.f | Start motor winding L@TS3 temperature | Winding, vikling, fase
A@ | RA2 | RK1 | RK@ | TDA1 |  | BTA@ | STMP | 1 | Hi1 | stVal | Start motor winding L@TS3 temperature alarm | Winding, vikling, fase
A@ | RA2 | RK1 | RK@ | TDA1 |  | BTA@ | STMP | 1 | Hi2 | stVal | Start motor winding L@TS3 temperature trip | Winding, vikling, fase
A@ | JF1 | KJ1 |  |  |  | BGC2 | SAXD | 1 | Dsp | mag.f | Upper guide bearing distance sensor Y
A@ | JF1 | KJ1 |  |  |  | BSG1 | SVBR | 1 | Hi2 | stVal | Upper guide bearing vibration trip
A@ | JF1 | KJ3 |  |  |  | BGC2 | SAXD | 1 | Dsp | mag.f | Turbine bearing distance sensor Y
A@ | JF1 | KJ3 |  |  |  | BSG1 | SVBR | 1 | Hi1 | stVal | Turbine bearing vibration alarm
A@ | JF1 | KJ2 |  |  |  | BGC2 | SAXD | 1 | Dsp | mag.f | Lower guide bearing distance sensor Y
A@ | JF1 | KJ2 |  |  |  | BSG1 | SVBR | 1 | Hi1 | stVal | Lower guide bearing vibration alarm
A@ | RB1 | LD1 |  |  |  |  | HOPL | 1 | OpnLimSpt | mxVal.f | Turbine stroke limiter set-point | Slagbegrenser, slagbegr
A@ | JF1 | KJ4 |  |  |  | BGC3 | SAXD | 1 | Dsp | mag.f | Thrust bearing distance sensor Z
A@ | LA1 | [5 empty] | AUNT | 1 | Stop | stVal | Unit stop in progress
A@ | LA1 | [5 empty] | AUNT | 1 | Pmp | stVal | Pumping mode
A@ | JF1 | KJ3 |  |  |  | BSG1 | SVBR | 1 | Hi2 | stVal | Turbine bearing vibration trip
A@ | RB1 | KA1 |  |  |  | BFA1 | SFLW | 1 | Flw | mag.f | Turbine flow measurement
A@ | JE1 | KF1 |  |  |  |  | MMXU | 1 | TotW | mag.f | Unit transformer active power
C1 | KA1 | KA1 |  | HQB1 |  | BLA2 | SLVL | 1 | Lev | mag.f | Trash rack downstream water level measurement
A@ | JE1 | KF1 |  |  |  |  | MMXU | 1 | Hz | mag.f | Unit transformer frequency
A@ | JE1 | KF1 |  |  |  |  | MMXU | 1 | PPV.phsAB | cVal.mag.f | Unit transformer voltage L1-L2
A@ | JE1 | KF1 |  |  |  |  | MMXU | 1 | PPV.phsBC | cVal.mag.f | Unit transformer voltage L2-L3
A@ | JE1 | KF1 |  |  |  |  | MMXU | 1 | PPV.phsCA | cVal.mag.f | Unit transformer voltage L3-L1
A@ | JE1 | KF1 |  |  |  |  | MMXU | 1 | PNV.phsA | cVal.mag.f | Unit transformer voltage L1-N
A@ | JE1 | KF1 |  |  |  |  | MMXU | 1 | PNV.phsB | cVal.mag.f | Unit transformer voltage L2-N
A@ | JE1 | KF1 |  |  |  |  | MMXU | 1 | PNV.phsC | cVal.mag.f | Unit transformer voltage L3-N
A@ | JE1 | KF1 |  |  |  |  | MMXU | 1 | A.phsA | cVal.mag.f | Unit transformer current L1
A@ | JE1 | KF1 |  |  |  |  | MMXU | 1 | A.phsB | cVal.mag.f | Unit transformer current L2
A@ | JE1 | KF1 |  |  |  |  | MMXU | 1 | A.phsC | cVal.mag.f | Unit transformer current L3
A@ | JE1 | KF1 |  |  |  |  | MMXU | 1 | AvPPVPhs | mag.f | Unit transformer avg voltage of the 3 phases
A@ | JF1 | KJ3 |  |  |  |  | HBRG | 16 | RdlDsp | mag.f | Turbine bearing sum max displacement
A@ | JF1 | KJ1 |  |  |  |  | HBRG | 16 | RdlDsp | mag.f | Upper guide bearing sum max displacement
A@ | JF1 | KJ2 |  |  |  |  | HBRG | 16 | RdlDsp | mag.f | Lower guide bearing sum max displacement
A@ | RA1 | LD1 |  |  |  |  | AVRG | 1 | ReqVAr | mag.f | Generator reactive power set-point | Settpunkt, innstilling, reference
A@ | RA1 | LD1 |  |  |  |  | HWGC | 1 | WSpt | mxVal.f | Generator active power set-point by operator
A@ | JF1 | KJ4 |  |  |  |  | HBRG | 16 | RdlDsp | mag.f | Thrust bearing sum max displacement
E@ | AA1 |  |  |  |  | BTA1 | STMP | 1 | Tmp | mag.f | Dam leakage water temperature
A@ | JE1 | KF1 |  |  |  |  | SIML | 1 | H2Oppm | mag.f | Unit transformer measurement of H2O in ppm
A@ | RA1 | [5 empty] | MMXU | 1 | TotVAr | mag.f | Generator reactive power
A@ | JE1 | KF1 |  |  |  |  | SIML | 1 | CmbuGas | mag.f | Unit transformer measurement of total dissolved combustible gases (TDCG)
A@ | JE1 | KF1 |  |  |  |  | SIML | 1 | O2ppm | mag.f | Unit transformer measurement of O2 in ppm
A@ | JE1 | KF1 |  |  |  |  | SIML | 1 | CH4ppm | mag.f | Unit transformer measurement of Methane in ppm
A@ | JE1 | KF1 |  |  |  |  | SIML | 1 | C2H4ppm | mag.f | Unit transformer measurement of Ethylane in ppm
A@ | JE1 | KF1 |  |  |  |  | SIML | 1 | C2H6ppm | mag.f | Unit transformer measurement of Ethane in ppm
A@ | JE1 | KF1 |  |  |  |  | SIML | 1 | CO2ppm | mag.f | Unit transformer measurement of CO2 in ppm
A@ | JE1 | KF1 |  |  |  |  | SIML | 1 | COppm | mag.f | Unit transformer measurement of CO in ppm
A@ | JE1 | KF1 |  |  |  |  | SIML | 1 | C2H2ppm | mag.f | Unit transformer measurement of Acetylene in ppm
A@ | JE1 | KF1 |  |  |  |  | SIML | 1 | H2ppm | mag.f | Unit transformer measurement of Hydrogen in ppm
A@ | RB1 | LD1 |  |  |  |  | HOPL | 1 | OpnLimEsp | mag.f | Turbine stroke limiter position | Slagbegrenser, slagbegr
A@ | RA1 | [5 empty] | MMXU | 1 | TotW | mag.f | Generator active power
C1 | KA1 |  |  |  |  | BLA1 | SLVL | 1 | Lev | mag.f | Intake water level measurement
A@ | RA1 | LD1 |  | QAB1 |  |  | XCBR | 1 | Pos | stVal | Excitation system switch | Magnbryter, magnetiseringsbryter
A@ | LA1 | [5 empty] | AUNT | 1 | Syn | stVal | Synchronisation trigger
A@ | RB1 | LD1 |  |  |  |  | HWGC | 1 | WSpt | mxVal.f | Turbine load set-point by operator
A@ | RB1 | LD1 |  |  |  |  | HOMX | 1 | ReqOpnMax | mag.f | Turbine PMax set-point | Hva er forskjell på pmax og ymax?
A@ | RB1 | LD1 |  |  |  |  | HSPC | 1 | ReqDrp | mag.f | Turbine droop
A@ | RB1 | LD1 |  |  |  |  | HWGC | 1 | ReqW | mag.f | Turbine power set-point
A@ | KA1 | [5 empty] | HVLV | 1 | PosPct | mag.f | Main valve opening in percent
H1 | KA1 | [5 empty] | HVLV | 1 | PosPct | mag.f | Outlet/draft tube valve opening in percent
A@ | JF1 | KA1 |  |  |  |  | HMBR | 1 | Pos | stVal | Mechanical brake position
A@ | JF1 | KA1 |  |  |  |  | HMBR | 1 | BrkOn | stVal | Mechanical brake on
A@ | JF1 | KA1 |  |  |  |  | HSPD | 1 | SpdBrk1 | stVal | Brake speed
A@ | KA1 | [5 empty] | HVLV | 1 | PosOpn | stVal | Main valve open
A@ | JF1 | KJ1 |  |  |  | BSG1 | SVBR | 1 | Vbr | mag.f | Upper guide bearing vibration (radial direction)
A@ | JF1 | KJ3 |  |  |  | BSG1 | SVBR | 1 | Vbr | mag.f | Turbine bearing vibration (radial direction)
A@ | JF1 | KJ2 |  |  |  | BSG1 | SVBR | 1 | Vbr | mag.f | Lower guide bearing vibration (radial direction)
A@ | JF1 | KJ4 |  |  |  | BSG1 | SVBR | 1 | Vbr | mag.f | Thrust bearing vibration (axial direction)
A@ | RA1 | LD1 |  |  |  |  | AUCG | 1 | ReqVol | mxVal.f | Generator voltage set-point
A@ | JF1 | KJ2 |  | FRA1 |  | BLA1 | SLVL | 1 | Lev | mag.f | Lower guide bearing oil level
A@ | JE1 | KF1 | HB1 |  |  | BLA1 | SLVL | 1 | Lev | mag.f | Unit transformer oil supply, oil level
C1 | KA2 | [5 empty] | HVLV | 1 | PosCls | stVal | Emergence closing valve closed
C1 | KA2 | [5 empty] | HVLV | 1 | PosOpn | stVal | Emergency closing valve open
E@ | KA1 | [5 empty] | HGTE | 1 | PosUp | stVal | Main inlet gate open
E@ | KA1 | [5 empty] | HGTE | 1 | PosDn | stVal | Main inlet gate closed
H1 | KA1 | [5 empty] | HGTE | 1 | PosUp | stVal | Outlet/draft tube gate open
H1 | KA1 | [5 empty] | HGTE | 1 | PosDn | stVal | Outlet/draft tube gate closed
A@ | JE1 | KF1 | HB1 |  |  | BLA1 | SLVL | 1 | Hi | stVal | Unit transformer oil supply, oil level alarm
A@ | KA1 | KB1 |  | NAD1 |  | BPC1 | SPRS | 1 | PresSv | instMag.f | Main valve primary seal pressure | Revisjonstetning
A@ | KA1 |  |  | MMA1 |  | BPA1 | SPRS | 2 | PresSv | instMag.f | Main valve hydraulic opening pressure | Åpnetrykk
A@ | KA1 | KB1 |  | NAD2 |  | BPC1 | SPRS | 1 | PresSv | instMag.f | Main valve secondary seal pressure | Hovedtetning
A@ | KA1 | JB1 |  | QMA1 |  | BPA2 | SPRS | 1 | PresSv | instMag.f | Main valve bypass valve closing pressure
H1 | KA1 |  |  | MMA1 |  | BGA1 | SDST | 1 | Dsp | mag.f | Draft tube valve hydraulic rod displacement
A@ | KA1 |  |  | MMA1 |  | BPA1 | SPRS | 1 | PresSv | instMag.f | Main valve hydraulic closing pressure | Lukketrykk
A@ | KA1 | JB1 |  | QMA1 |  | BPA1 | TPRS | 1 | PresSv | instMag.f | Main valve bypass valve opening pressure
E@ | KA1 |  |  |  |  | BFA1 | SFLW | 1 | Flw | mag.f | Reservoir bypass gate, flow
E@ | KA1 | [5 empty] | HGTE | 1 | Pos | mag.f | Reservoir bypass gate, Position
E@ | KA2 | KA1 |  |  |  |  | HGTE | 1 | Pos | mag.f | Maintenance gate position
E@ | AA@ | LE1 |  |  |  | GBA1 | SBAT | 1 | UntnVpct | mag.f | Dam, sensor battery charge
E@ | AA@ | LE1 |  |  |  | BLA1 | SLVL | 1 | Snr | mag.f | Dam, sensor signal to noise ratio
E@ | AA1 |  |  |  |  | BPA1 | SPRS | 1 | Pres | mag.f | Water pressure
A@ | RA1 | HE1 | HB1 |  |  | BFA1 | SFLW | 1 | Lo1 | stVal | Generator cooling water circulation low alarm
A@ | LA1 | [5 empty] | AUNT | 1 | Tur | stVal | Unit turning
A@ | RA1 | HE1 |  |  |  | BTA1@ | STMP | 1 | Tmp | mag.f | Generator air cooler @CS3 cold air temperature
A@ | LA1 | [5 empty] | AUNT | 1 | StrtNE | stVal | Unit start ready not excited
A@ | LA1 | [5 empty] | AUNT | 1 | Synd | stVal | Generating mode, not islanded
A@ | LA1 | [5 empty] | AUNT | 1 | TurE | stVal | Unit turning excited
A@ | LA1 | [5 empty] | AUNT | 1 | StrtE | stVal | Unit start ready excited
A@ | LA1 | [5 empty] | AUNT | 1 | TurNE | stVal | Unit turning not excited
A@ | LA1 | [5 empty] | AUNT | 1 | StndStl | stVal | Stand-still detection
A@ | JE1 | KF1 | HE1 |  |  | BTA1@ | STMP | 1 | Tmp | mag.f | Unit transformer oil cooler @CS3 cold oil temperature
A@ | JE1 | KF1 | HE1 |  |  | BTA2@ | STMP | 1 | Tmp | mag.f | Unit transformer oil cooler @CS3 warm oil temperature
A@ | JE1 | KF1 |  |  |  | BTA1 | STMP | 1 | Hi2 | stVal | Unit transformer oil temperature trip
A@ | JE1 | KF1 |  |  |  | BTA1 | STMP | 1 | Hi1 | stVal | Unit transformer oil temperature alarm
A@ | JE1 | KF1 |  |  |  | BTA1 | STMP | 1 | Tmp | mag.f | Unit transformer oil temperature
A@ | JE1 | KF1 |  |  |  |  | MMXU | 1 | AvAPhs | mag.f | Unit transformer avg current of the 3 phases
A@ | JE1 | KF1 |  | WKA1 |  | BTA1 | STMP | 1 | Tmp | mag.f | Unit transformer core temperature
A@ | JE1 | KF1 |  |  |  | BLA1 | SLVL | 1 | Lev | mag.f | Unit transformer oil level
A@ | JE1 | KF1 |  |  |  |  | SIML | 1 | H2Opct | mag.f | Unit transformer measurement of H2O in percent
E@ | AA@ |  |  |  |  | BLA1 | SLVL | 1 | LevOfs | setMag.f | Dam, installation offset height above sea level
| LE40 |  |  |  |  | BTA1 | MMET | 1 | EnvTmp | mag.f | Ambient air temperature
E@ | [5 empty] | BTA1 | STMP | 1 | Tmp | mag.f | Reservoir water temperature
E@ | AA@ |  |  |  |  | BTA1 | STMP | 1 | Tmp | mag.f | Dam, water temperature
E@ | AA@ |  |  | RQB1 |  | BPA1 | SPRS | 1 | Pres | mag.f | Dam, pore pressure
E@ | AA@ |  |  |  |  | BLA1 | SLVL | 1 | Lev | mag.f | Dam, calculated water level above sea level
E@ | LE40 |  |  |  |  | BFA1 | MMET | 1 | RnFll | mag.f | Rainfall/precipitation
E@ | LE40 |  |  |  |  | BPA1 | MMET | 1 | EnvPres | mag.f | Ambient air pressure
E@ | AA@ |  |  | RQB1 |  | GBA1 | SBAT | 1 | UntnVpct | mag.f | Dam, pore pressure sensor battery charge
C1 | [6 empty] | HNHD | 1 | DifPres | mag.f | Calculated head loss
E@ | LE40 |  |  |  |  | BGE1 | MMET | 1 | HorWdDir | mag.f | Wind direction
E@ | LE40 |  |  |  |  | BFA1 | MMET | 1 | HorWdSpd | mag.f | Wind speed
E@ | LE40 |  |  |  |  | BMA1 | MMET | 1 | EnvHum | mag.f | Humidity
C1 | KA1 | KA1 |  | HQB1 |  |  | HNHD | 1 | DifPres | mag.f | Trash rack head loss
A@ | LA1 | [5 empty] | AUNT | 1 | Strt | stVal | Unit autostart enabled
E@ | AA@ | [5 empty] | HDLS | 1 | Flw | mag.f | Dam, leakage calculation
E@ | [6 empty] | HLVL | 1 | LevM | mag.f | Reservoir water level calculation
E@ | AA@ |  |  |  |  | BFA1 | SFLW | 401 | Flw | mag.f | Dam, leakage measurement hourly
E@ | AA@ |  |  |  |  | BFA1 | SFLW | 415 | Flw | mag.f | Dam, leakage measurement hourly minumum
E@ | AA@ |  |  |  |  | BFA1 | SFLW | 416 | Flw | mag.f | Dam, leakage measurement hourly maximum
E@ | AA@ |  |  |  |  | BFA1 | SFLW | 417 | Flw | mag.f | Dam, leakage measurement hourly average
E@ | AA@ |  |  | RQB1 |  | BLA1 | SLVL | 1 | Lev | mag.f | Dam, pore pressure calculated water level above sea level
C1 | PF1 |  |  |  |  | BLA1 | SLVL | 1 | Lev | mag.f | Air cushion chamber level
E@ | [5 empty] | BLA1 | SLVL | 1 | Lev | mag.f | Reservoir water level measurement
C1 | KA1 | KA1 |  | HQB1 |  | BLA1 | SLVL | 1 | Lev | mag.f | Trash rack upstream water level measurement
E@ | KA1 | KA1 |  |  |  |  | HGTE | 1 | Pos | mag.f | Flood gate posistion
E@ | KA3 | KA1 |  |  |  |  | HGTE | 1 | Pos | mag.f | Drainage gate posistion (Drenering/tappeluke)
C1 | JB1 |  |  |  |  | BPA1 | SPRS | 1 | Pres | mag.f | Intake tunnel pressure
C1 | KA2 | [5 empty] | HGTE | 1 | Pos | mag.f | Emergency closing valve position
E@ | AA@ |  |  |  |  | BFA1 | SFLW | 1 | Flw | mag.f | Dam, leakage measurement
C1 | KA1 | [5 empty] | HGTE | 1 | Pos | mag.f | Intake gate position
A@ | RB1 | KA1 |  |  |  |  | HTGV | 1 | PosPct | mag.f | Guide vanes opening in percent | Pådrag Francis
A@ | KA1 |  |  |  |  | BPA1 | SPRS | 1 | Hi1 | stVal | Main inlet valve, inlet pressure high trip (sjakttrykk) | Penstock pressure, sjakttrykk
A@ | KA1 |  |  |  |  | BPA1 | SPRS | 1 | Pres | mag.f | Main inlet valve, inlet pressure (sjakttrykk) | Penstock pressure, sjakttrykk
A@ | KA1 |  |  |  |  | BPA1 | SPRS | 1 | Hi2 | stVal | Main inlet valve, inlet pressure high alarm (sjakttrykk) | Penstock pressure, sjakttrykk
E@ | [5 empty] | BLA1 | SLVL | 416 | Lev | mag.f | Reservoir water level hourly average
E@ | [5 empty] | BLA1 | SLVL | 401 | Lev | mag.f | Reservoir water level hourly
E@ | [5 empty] | BLA1 | SLVL | 416 | Lev | mag.f | Reservoir water level hourly maximum
E@ | [5 empty] | BLA1 | SLVL | 415 | Lev | mag.f | Reservoir water level hourly minimum
A@ | RA1 | HE1 |  |  |  | BTA2@ | STMP | 1 | Tmp | mag.f | Generator air cooler @CS3 warm air temperature
A@ | RA1 | HE1 |  | EGC@ |  | BTA1 | STMP | 1 | Tmp | mag.f | Generator air cooler @CS1 cold water temperature
A@ | RA1 | HE1 |  | EGC@ |  | BTA2 | STMP | 1 | Tmp | mag.f | Generator air cooler @CS1 warm water temperature
A@ | RA1 | HE1 | HB1 |  |  | BFA1 | SFLW | 1 | Lo2 | stVal | Generator cooling water circulation low trip
A@ | RA1 | HE1 | HB1 |  |  | BTA2 | STMP | 1 | Hi2 | stVal | Generator air coolers warm water temperature high trip
A@ | RA1 | HE1 | HB1 |  |  | BTA1 | STMP | 1 | Hi2 | stVal | Generator air coolers cold water temperature high trip
A@ | RA1 | HE1 | HB1 |  |  | BTA2 | STMP | 1 | Hi1 | stVal | Generator air coolers warm water temperature high alarm
A@ | RA1 | HE1 | HB1 |  |  | BTA1 | STMP | 1 | Hi1 | stVal | Generator air coolers cold water temperature high alarm
A@ | JF1 | KJ1 |  | EGC@ |  | BTA1 | STMP | 1 | Tmp | mag.f | Upper guide bearing cooler @CS1 cooling water temperature trip
A@ | JF1 | KJ1 |  | EGC@ |  | BTA1 | STMP | 1 | Hi1 | stVal | Upper guide bearing cooler @CS1 cooling water temperature alarm
A@ | JF1 | KJ1 |  | EGC@ |  | BTA1 | STMP | 1 | Hi2 | stVal | Upper guide bearing cooler @CS1 cooling water temperature
A@ | JF1 | KJ3 |  | EGC@ |  | BTA1 | STMP | 1 | Tmp | mag.f | Turbine bearing cooler @CS1 cooling water temperature trip
A@ | JF1 | KJ3 |  | EGC@ |  | BTA1 | STMP | 1 | Hi1 | stVal | Turbine bearing cooler @CS1 cooling water temperature alarm
A@ | JF1 | KJ3 |  | EGC@ |  | BTA1 | STMP | 1 | Hi2 | stVal | Turbine bearing cooler @CS1 cooling water temperature
A@ | JF1 | KJ1 |  | EGC1 |  | BFA1 | SFLW | 1 | Lo1 | stVal | Upper guide bearing cooling water circulation low alarm
A@ | JF1 | KJ1 |  | EGC1 |  | BFA1 | SFLW | 1 | Lo2 | stVal | Upper guide bearing cooling water circulation low trip
A@ | JF1 | KJ3 |  | EGC1 |  | BFA1 | SFLW | 1 | Lo2 | stVal | Turbine bearing cooling water circulation low trip
A@ | JF1 | KJ3 |  | EGC1 |  | BFA1 | SFLW | 1 | Lo1 | stVal | Turbine bearing cooling water circulation low alarm
A@ | JF1 | KJ4 | HB1 | EGC@ |  | BTA1 | STMP | 1 | Tmp | mag.f | Thrust bearing cooler @CS1 cooling water temperature trip
A@ | JF1 | KJ4 | HB1 | EGC@ |  | BTA1 | STMP | 1 | Hi1 | stVal | Thrust bearing cooler @CS1 cooling water temperature alarm
A@ | JF1 | KJ4 | HB1 | EGC@ |  | BTA1 | STMP | 1 | Hi2 | stVal | Thrust bearing cooler @CS1 cooling water temperature
A@ | JE1 | KF1 | HE1 | EGC@ |  | BTA2 | STMP | 1 | Tmp | mag.f | Unit transformer oil cooler @CS1 warm water temperature
A@ | JE1 | KF1 | HE1 | EGC@ |  | BTA1 | STMP | 1 | Tmp | mag.f | Unit transformer oil cooler @CS1 cold water temperature
A@ | RA1 | RK1 |  | UQA1 |  | BTA1 | STMP | 1 | Tmp | mag.f | Stator core joint temperature alarm | Deleskjøt
A@ | RA1 | RK1 |  | UQA1 |  | BTA1 | STMP | 1 | Hi2 | stVal | Stator core joint temperature trip | Deleskjøt
A@ | RA1 | RK1 |  | UQA1 |  | BTA1 | STMP | 1 | Hi1 | stVal | Stator core joint temperature | Deleskjøt
A@ | RB1 | HB1 |  |  |  | BPA1 | SPRS | 1 | Pres | mag.f | Turbine, pressurized oil supply, pressure | Oljetrykksanlegg, trykkakkumulator
A@ | RB1 | HB1 |  | CMA1 |  | BLA1 | SLVL | 1 | Lev | mag.f | Turbine, pressurized oil supply tank, level | Kasse, oljetrykksanlegg
A@ | RB1 | HB1 |  | CMA1 |  | BTA1 | STMP | 1 | Tmp | mag.f | Turbine, pressurized oil supply tank, temperature | Kasse, oljetrykksanlegg
E@ | KA3 |  |  |  |  | BFA1 | SFLW | 1 | Flw | mag.f | Drainage gate flow measurement (Drenering/tappeluke)
H1 | KA1 | [5 empty] | HGTE | 1 | PosPct | mag.f | Outlet/draft tube gate opening in percent
H1 | KA1 | [5 empty] | HVLV | 1 | PosUp | stVal | Outlet/draft tube valve closed
H1 | KA1 | [5 empty] | HVLV | 1 | PosDn | stVal | Outlet/draft tube valve open
A@ | JF1 | LE1 |  |  |  |  | HSPD | 1 | SpdOv | stVal | Over-speed detection
A@ | JF1 | LE1 |  |  |  |  | HSPD | 1 | SpdPct | mag.f | Rotational speed (%) | Rotasjonshastighet, omdreiningshastighet
A@ | JF1 | LE1 |  |  |  |  | HSPD | 1 | Spd | mag.f | Rotational speed
A@ | JF1 | KJ4 |  |  |  | BGC1 | SAXD | 1 | Dsp | mag.f | Thrust bearing distance sensor X
A@ | JF1 | KJ2 |  |  |  | BGC1 | SAXD | 1 | Dsp | mag.f | Lower guide bearing distance sensor X
A@ | JF1 | KJ3 |  |  |  | BGC1 | SAXD | 1 | Dsp | mag.f | Turbine bearing distance sensor X
A@ | JF1 | KJ1 |  |  |  | BGC1 | SAXD | 1 | Dsp | mag.f | Upper guide bearing distance sensor X | Øvre styrelager
A@ | RA1 | RK1 | RK3 | UNA@ |  | BTA1 | STMP | 1 | Tmp | mag.f | Stator core tooth @CS1 phase L3 temperature | Tann, tooth, stator core tooth, statortann
A@ | RA1 | RK1 | RK3 | UNA@ |  | BTA1 | STMP | 1 | Hi2 | stVal | Stator core tooth @CS1 phase L3 temperature trip | Tann, tooth, stator core tooth, statortann
A@ | RA1 | RK1 | RK3 | UNA@ |  | BTA1 | STMP | 1 | Hi1 | stVal | Stator core tooth @CS1 phase L3 temperature alarm | Tann, tooth, stator core tooth, statortann
A@ | RA1 | RK1 | RK3 |  |  | BTA1 | STMP | 1 | Tmp | mag.f | Stator core phase L3 temperature | Statorblikk
A@ | RA1 | RK1 | RK3 |  |  | BTA1 | STMP | 1 | Hi2 | stVal | Stator core phase L3 temperature trip | Statorblikk
A@ | RA1 | RK1 | RK3 |  |  | BTA1 | STMP | 1 | Hi1 | stVal | Stator core phase L3 temperature alarm | Statorblikk
A@ | JF1 | KJ2 |  | EGC1 |  | BFA@ | SFLW | 1 | Lo2 | stVal | Lower guide bearing cooling water circulation trip | Nedre styrelager
A@ | JF1 | KJ2 |  | FRA1 |  | BFA@ | SFLW | 1 | Flw | mag.f | Lower guide bearing oil flow | Nedre styrelager
A@ | RA1 | RK1 | RK3 | UNA1 |  | BTA1 | STMP | 1 | Tmp | mag.f | Stator core tooth phase L3 temperature | Tann, tooth, stator core tooth, statortann
A@ | RA1 | RK1 | RK3 | UNA1 |  | BTA1 | STMP | 1 | Hi2 | stVal | Stator core tooth phase L3 temperature trip | Tann, tooth, stator core tooth, statortann
A@ | RA1 | RK1 | RK3 | UNA1 |  | BTA1 | STMP | 1 | Hi1 | stVal | Stator core tooth phase L3 temperature alarm | Tann, tooth, stator core tooth, statortann
A@ | RA1 | RK1 | RK1 | TDA@ |  | BTA1 | STMP | 1 | Tmp | mag.f | Stator core winding @CS1 phase L1 temperature | Spor, slot, winding, vikling, statorblikk spor, fase
A@ | RA1 | RK1 | RK1 | TDA@ |  | BTA1 | STMP | 1 | Hi2 | stVal | Stator core winding @CS1 phase L1 temperature trip | Spor, slot, winding, vikling, statorblikk spor, fase
A@ | RA1 | RK1 | RK1 | TDA@ |  | BTA1 | STMP | 1 | Hi1 | stVal | Stator core winding @CS1 phase L1 temperature alarm | Spor, slot, winding, vikling, statorblikk spor, fase
A@ | RA1 | RK1 | RK1 | UNA@ |  | BTA1 | STMP | 1 | Tmp | mag.f | Stator core tooth @CS1 phase L1 temperature | Tann, tooth, stator core tooth, statortann
A@ | RA1 | RK1 | RK1 | UNA@ |  | BTA1 | STMP | 1 | Hi2 | stVal | Stator core tooth @CS1 phase L1 temperature trip | Tann, tooth, stator core tooth, statortann
A@ | RA1 | RK1 | RK1 | UNA@ |  | BTA1 | STMP | 1 | Hi1 | stVal | Stator core tooth @CS1 phase L1 temperature alarm | Tann, tooth, stator core tooth, statortann
A@ | RA1 | RK1 | RK1 |  |  | BTA1 | STMP | 1 | Tmp | mag.f | Stator core phase L1 temperature | Statorblikk
A@ | RA1 | RK1 | RK1 |  |  | BTA1 | STMP | 1 | Hi2 | stVal | Stator core phase L1 temperature trip | Statorblikk
A@ | RA1 | RK1 | RK1 |  |  | BTA1 | STMP | 1 | Hi1 | stVal | Stator core phase L1 temperature alarm | Statorblikk
A@ | RA1 | RK1 | RK1 | UNA1 |  | BTA1 | STMP | 1 | Tmp | mag.f | Stator core tooth phase L1 temperature | Tann, tooth, stator core tooth, statortann
A@ | RA1 | RK1 | RK1 | UNA1 |  | BTA1 | STMP | 1 | Hi2 | stVal | Stator core tooth phase L1 temperature trip | Tann, tooth, stator core tooth, statortann
A@ | RA1 | RK1 | RK2 | UNA1 |  | BTA1 | STMP | 1 | Hi2 | stVal | Stator core tooth phase L2 temperature trip | Tann, tooth, stator core tooth, statortann
A@ | RA1 | RK1 | RK2 | UNA1 |  | BTA1 | STMP | 1 | Hi1 | stVal | Stator core tooth phase L2 temperature alarm | Tann, tooth, stator core tooth, statortann
A@ | RA1 | RK1 | RK2 | TDA@ |  | BTA1 | STMP | 1 | Tmp | mag.f | Stator core winding @CS1 phase L2 temperature | Spor, slot, winding, vikling, statorblikk spor, fase
A@ | RA1 | RK1 | RK2 | TDA@ |  | BTA1 | STMP | 1 | Hi2 | stVal | Stator core winding @CS1 phase L2 temperature trip | Spor, slot, winding, vikling, statorblikk spor, fase
A@ | RA1 | RK1 | RK2 | TDA@ |  | BTA1 | STMP | 1 | Hi1 | stVal | Stator core winding @CS1 phase L2 temperature alarm | Spor, slot, winding, vikling, statorblikk spor, fase
A@ | RA1 | RK1 | RK2 | UNA@ |  | BTA1 | STMP | 1 | Tmp | mag.f | Stator core tooth @CS1 phase L2 temperature | Tann, tooth, stator core tooth, statortann
A@ | RA1 | RK1 | RK2 | UNA@ |  | BTA1 | STMP | 1 | Hi2 | stVal | Stator core tooth @CS1 phase L2 temperature trip | Tann, tooth, stator core tooth, statortann
A@ | RA1 | RK1 | RK2 | UNA@ |  | BTA1 | STMP | 1 | Hi1 | stVal | Stator core tooth @CS1 phase L2 temperature alarm | Tann, tooth, stator core tooth, statortann
A@ | RA1 | RK1 | RK2 |  |  | BTA1 | STMP | 1 | Tmp | mag.f | Stator core phase L2 temperature | Statorblikk
A@ | RA1 | RK1 | RK2 |  |  | BTA1 | STMP | 1 | Hi2 | stVal | Stator core phase L2 temperature trip | Statorblikk
A@ | RA1 | RK1 | RK2 |  |  | BTA1 | STMP | 1 | Hi1 | stVal | Stator core phase L2 temperature alarm | Statorblikk
A@ | RA1 | RK1 | RK2 | UNA1 |  | BTA1 | STMP | 1 | Tmp | mag.f | Stator core tooth phase L2 temperature | Tann, tooth, stator core tooth, statortann
A@ | RA1 | RK1 | RK1 | UNA1 |  | BTA1 | STMP | 1 | Hi1 | stVal | Stator core tooth phase L1 temperature alarm | Tann, tooth, stator core tooth, statortann
A@ | RA1 | LD1 |  | TAA1 | TAA2 | BTA1 | STMP | 1 | Tmp | mag.f | Excitation system winding L2 temperature | Winding, vikling, fase
A@ | RA1 | LD1 |  | TAA1 | TAA3 | BTA1 | STMP | 1 | Tmp | mag.f | Excitation system winding L3 temperature | Winding, vikling, fase
A@ | JF1 | KJ1 |  | FRA1 |  | BLA@ | SLVL | 1 | Hi1 | stVal | Upper guide bearing oil level high alarm
A@ | JF1 | KJ2 |  | FRA1 |  | BLA@ | SLVL | 1 | Hi1 | stVal | Lower guide bearing oil level high alarm
A@ | JF1 | KJ4 |  | FRA1 |  | BPC@ | SPRS | 1 | Pres | mag.f | Thrust bearing segment @CS3 oil pressure
A@ | JF1 | KJ4 |  | FRA1 |  | BPC@ | SPRS | 1 | Lo1 | stVal | Thrust bearing segment @CS3 oil pressure low alarm
A@ | JF1 | KJ4 |  | FRA1 |  | BPC@ | SPRS | 1 | Hi2 | stVal | Thrust bearing segment @CS3 oil pressure high trip
A@ | JF1 | KJ4 |  | FRA1 |  | BPC@ | SPRS | 1 | Hi1 | stVal | Thrust bearing segment @CS3 oil pressure high alarm
A@ | JF1 | KJ4 |  | FRA1 |  | BPC1 | SPRS | 1 | Lo2 | stVal | Thrust bearing oil pressure low trip
A@ | JF1 | KJ4 |  | FRA1 |  | BPC1 | SPRS | 1 | Hi2 | stVal | Thrust bearing oil pressure high trip
A@ | JF1 | KJ4 |  | FRA1 |  | BPC1 | SPRS | 1 | Hi1 | stVal | Thrust bearing oil pressure high alarm
A@ | JF1 | KJ4 |  | FRA1 |  | BPC1 | SPRS | 1 | Lo1 | stVal | Thrust bearing oil pressure low alarm
A@ | JF1 | KJ4 |  | FRA1 |  | BPC1 | SPRS | 1 | Pres | mag.f | Thrust bearing oil pressure
A@ | JF1 | KJ2 |  |  |  | BSG1 | SVBR | 1 | Hi2 | stVal | Lower guide bearing vibration trip
A@ | RA1 | HE1 | HB1 |  |  | BFA1 | SFLW | 1 | Flw | mag.f | Generator cooling water circulation flow
A@ | RA1 | LD1 |  | TAA1 | TAA1 | BTA1 | STMP | 1 | Hi2 | stVal | Excitation system winding L1 temperature trip | Winding, vikling, fase
A@ | RA1 | LD1 |  | TAA1 | TAA2 | BTA1 | STMP | 1 | Hi2 | stVal | Excitation system winding L2 temperature trip | Winding, vikling, fase
A@ | RA1 | LD1 |  | TAA1 | TAA3 | BTA1 | STMP | 1 | Hi2 | stVal | Excitation system winding L3 temperature trip | Winding, vikling, fase
A@ | RA1 | LD1 |  | TAA1 | TAA1 | BTA1 | STMP | 1 | Hi1 | stVal | Excitation system winding L1 temperature alarm | Winding, vikling, fase
A@ | RA1 | LD1 |  | TAA1 | TAA2 | BTA1 | STMP | 1 | Hi1 | stVal | Excitation system winding L2 temperature alarm | Winding, vikling, fase
A@ | RA1 | LD1 |  | TAA1 | TAA3 | BTA1 | STMP | 1 | Hi1 | stVal | Excitation system winding L3 temperature alarm | Winding, vikling, fase
A@ | RB1 | LD1 |  |  |  |  | HSPC | 1 | Spd | mag.f | Turbine frequency | Hz
A@ | JF1 | KJ4 |  |  |  | BGC2 | SAXD | 1 | Dsp | mag.f | Thrust bearing distance sensor Y
A@ | JF1 | KJ1 |  |  |  | BSG1 | SVBR | 1 | Hi1 | stVal | Upper guide bearing vibration alarm
A@ | KA1 |  |  |  |  | BPA1 | SPRS | 1 | Lo2 | stVal | Main inlet valve, inlet pressure low alarm (sjakttrykk) | Penstock pressure, sjakttrykk
A@ | KA1 |  |  |  |  | BPA1 | SPRS | 1 | Lo1 | stVal | Main inlet valve, inlet pressure low trip (sjakttrykk) | Penstock pressure, sjakttrykk